## Sheet1
Gateway Modbus address mapping for Mk5 controller
XD4150W1 gen. 1 , WUX111 | Mk5 controller must be in Mk5 CAN profile !
1900525885 - XD - Graphic 2.64.1.0 | Standalone Dryer
7/24/2024 9:38:32 AM
Coils
Name (1/0) | Coil
Running/Stopped | 1
Load/Unload | 2
General Warning | 3
General ShutdownWarning | 4
General Shutdown | 5
General Service | 6
General StartFailure | 7
Emergency Stop | 8
Automatic/Manual | 9
Remote/Local | 10
Analog Inputs |  |  | Registers
Name | Type | Unit | Status | Value | Value Interpretation
进出口压差 | Pressure (mBar) | mBar | 15 | 16 | Values are S16. 32767 = Sensor error.
再生阀压差 | Pressure (mBar) | mBar | 17 | 18
冷干机出口 | Pressure (mBar) | mBar | 21 | 22
干燥器进口 | Temperature | 0.1 °C | 25 | 26
加热器出口 | Temperature | 0.1 °C | 27 | 28
容器A底端温度 | Temperature | 0.1 °C | 29 | 30
容器B底端温度 | Temperature | 0.1 °C | 31 | 32
冷却器1空气进口温度 | Temperature | 0.1 °C | 35 | 36
干燥器压力露点 | Temperature | 0.1 °C | 47 | 48
再生阀关闭比例 | Percentage | % | 179 | 180
Digital Inputs |  |  | Registers
Name |  |  | Status | Value | Functional Interpretation 0/1
远程启动/停机 |  |  | 501 | 502 | 开 / 关
紧急停机 |  |  | 503 | 504 | 开 / 关
接触加载 |  |  | 505 | 506 | 卸载 / 加载
加热器保险丝 |  |  | 507 | 508 | 开 / 关
过热转换 |  |  | 513 | 514 | 开 / 关
冷却器排污失败 |  |  | 521 | 522 | 开 / 关
冷却器2排放故障 |  |  | 523 | 524 | 开 / 关
阀 V1打开 |  |  | 525 | 526 | 开 / 关
阀 V1关闭 |  |  | 527 | 528 | 开 / 关
阀 V2打开 |  |  | 529 | 530 | 开 / 关
阀 V2关闭 |  |  | 531 | 532 | 开 / 关
阀 V3打开 |  |  | 533 | 534 | 开 / 关
阀 V3关闭 |  |  | 535 | 536 | 开 / 关
阀 V4打开 |  |  | 537 | 538 | 开 / 关
阀 V4关闭 |  |  | 539 | 540 | 开 / 关
阀 V8打开 |  |  | 545 | 546 | 开 / 关
阀 V8关闭 |  |  | 547 | 548 | 开 / 关
阀 V9打开 |  |  | 549 | 550 | 开 / 关
阀 V9关闭 |  |  | 551 | 552 | 开 / 关
阀 V13打开 |  |  | 557 | 558 | 开 / 关
阀 V13关闭 |  |  | 559 | 560 | 开 / 关
阀 V14打开 |  |  | 561 | 562 | 开 / 关
阀 V14关闭 |  |  | 563 | 564 | 开 / 关
阀 V16打开 |  |  | 565 | 566 | 开 / 关
阀 V16关闭 |  |  | 567 | 568 | 开 / 关
阀 V17打开 |  |  | 569 | 570 | 开 / 关
阀 V17关闭 |  |  | 571 | 572 | 开 / 关
阀 V23打开 |  |  | 577 | 578 | 开 / 关
阀 V23关闭 |  |  | 579 | 580 | 开 / 关
阀 V30打开 |  |  | 581 | 582 | 开 / 关
阀 V30关闭 |  |  | 583 | 584 | 开 / 关
|  |  | Bit | Description (1/0)
|  |  | 0 | PreWarning
|  |  | 1 | Warning
|  |  | 2 | ShutdownWarning
|  |  | 3 | Shutdown
|  |  | 4 | Service
|  |  | 5 | Permissive
|  |  | 6 | Sensor Error
|  |  | 7 | Set/Not set
|  |  | 8 | SPM valid measurement
|  |  | 13 | PrePermissive
Analog Outputs |  |  | Registers
Name | Type | Unit | Value |  | Value Interpretation
再生阀%关闭 | Percentage Out | 0.01 % | 2501 |  | Values are S16.
Digital Outputs |  |  | Registers
Name |  |  | Value |  | Functional Interpretation 0/1
冷干机马达启动 |  |  | 2551 |  | 开 / 关
普通警告 |  |  | 2552 |  | 开 / 关
普通停机 |  |  | 2553 |  | 开 / 关
PDP警报 |  |  | 2554 |  | 开 / 关
冷干机卸载 |  |  | 2555 |  | 卸载 / 加载
阀V1 打开 |  |  | 2560 |  | 开 / 关
阀V1 关闭 |  |  | 2561 |  | 开 / 关
阀V2 打开 |  |  | 2562 |  | 开 / 关
阀V2 关闭 |  |  | 2563 |  | 开 / 关
阀V3 打开 |  |  | 2564 |  | 开 / 关
阀V3 关闭 |  |  | 2565 |  | 开 / 关
阀V4 打开 |  |  | 2566 |  | 开 / 关
阀V4 关闭 |  |  | 2567 |  | 开 / 关
阀V5 关闭 |  |  | 2568 |  | 开 / 关
阀V8 打开 |  |  | 2569 |  | 开 / 关
阀V8 关闭 |  |  | 2570 |  | 开 / 关
阀V9 打开 |  |  | 2571 |  | 开 / 关
阀V9 关闭 |  |  | 2572 |  | 开 / 关
阀V13 打开 |  |  | 2573 |  | 开 / 关
阀V13 关闭 |  |  | 2574 |  | 开 / 关
主加热器 |  |  | 2575 |  | 开 / 关
调解加热器 |  |  | 2576 |  | 开 / 关
阀V14 打开 |  |  | 2578 |  | 开 / 关
阀V14 关闭 |  |  | 2579 |  | 开 / 关
阀V16 打开 |  |  | 2580 |  | 开 / 关
阀V16 关闭 |  |  | 2581 |  | 开 / 关
阀V17 打开 |  |  | 2582 |  | 开 / 关
阀V17 关闭 |  |  | 2583 |  | 开 / 关
阀V22 打开 |  |  | 2584 |  | 开 / 关
阀V22 关闭 |  |  | 2585 |  | 开 / 关
阀V23 打开 |  |  | 2586 |  | 开 / 关
阀V23 关闭 |  |  | 2587 |  | 开 / 关
阀V30 打开 |  |  | 2588 |  | 开 / 关
阀V30 关闭 |  |  | 2589 |  | 开 / 关
Counters |  |  | Registers
Name |  | Unit | Value = (65536 x W2) + W1 |  | Reference counters for % calculation
|  |  | Value W2 | Value W1
干燥机运行时间 |  | s | 1001 | 1002
干燥机加载时间 |  | s | 1003 | 1004
实际显示时间 |  | s | 1005 | 1006
程序显示时间 |  | s | 1007 | 1008
实际半循环时间 |  | s | 1009 | 1010
程序半循环时间 |  | s | 1011 | 1012
容器A再生循环 |  | Count | 1013 | 1014
容器B再生循环 |  | Count | 1015 | 1016
节能PDP传感器 |  | Percent | 1017 | 1018
控制器运行时间 |  | s | 1019 | 1020
紧急停机 |  | Count | 1021 | 1022
Special Alarms |  |  | Registers
Name |  |  | Status
露点高 |  |  | 2725
扩展模块交流 |  |  | 2742
干燥机卸载 |  |  | 2805
加热温度低 |  |  | 2829
5号阀位置错误 |  |  | 2830
|  |  | Bit | Description (1/0)
|  |  | 0 | PreWarning
|  |  | 1 | Warning
|  |  | 3 | Shutdown
Machine Control Mode
Register 702 - LO byte
Name | Value
2a - Local Start/Stop & Pressure Sensing | 0
3a - Remote Start/Stop, Local Pressure Sensing | 1
4a - Communication Start/stop, Local Pressure Sensing | 2
2b - Local Start/Stop, Digital Contact Pressure Sensing | 16
3b - Remote Start/Stop, Digital Contact Pressure Sensing | 17
4b - Communication Start/Stop & SPS Control | 18
4c - Communication Start/Stop & Speed Control | 34
4d - ES/EQ/ECO Controlled | 50
2e - Local Start/Stop & 4-20mA Speed Control | 64
3e - Remote Start/Stop & 4-20mA Speed Control | 65
Machine Mechanical State
Register 701 - HI byte
Name | Value
Stop | 1
Running | 2
General Status
Register 703
Name | Bit
PreWarning | 0
General Warning | 1
General Shutdown Warning | 2
General Shutdown | 3
General Service | 4
General Start Failure | 5
Emergency Stop | 6
Manual/Automatic | 7
Local/Remote | 8
Week Timer | 9
PreWarning Service Running Hours | 10
- | 11
PreWarning Service Analog Input | 12
PrePermissive | 13
Test Mode | 14
Normal or Special Test Sequence | 15
Regulation Parameters
Name | Register | Value Read | Value Write |  |  | Info
External Set Point control | 871 | not applicable | MIN value =< value in 0.1°C =< MAX value
Commands - LAN mode
Name | Register | Value Read | Value Write | Info
Start | 2001 | n/a | 1 | Start the main machine
Stop | 2001 | n/a | 2 | Stop the main machine